[image: image1.wmf]
[image: image3.wmf]
Active Thermal Management

             The trusted name in thermal protection
Parts list – before proceeding, check that you have received all of the following:

(1) System 2 Kit control amplifier

(2) or (4) (depending on model) 120mm fans

(2) or (4) finger guards

(1) power supply

(2) thermistors
(2) magnets

System 2 Kit and 2 + 2 Kit Instructions 

NOTE:  Read these instructions, as changes have recently been made to simplify installation. Changes are shown underlined.
The Active Thermal Management System 2 and 2 + 2 kits are self-contained ventilating systems for small-to-midsize enclosures with moderate heat loads. While similar in operation to the System 2, the components are not mounted to a common base, but are separated by function to allow maximum flexibility in installation. The major individual components are the control box, power supply, temperature sensors  (thermistors)  and two (2) or four (2+2) 4.7" fans.

A quick overview of the installation process:

1. The fans are located at the point(s) where heated air is to be exhausted from the enclosure.  If desired, 1 or 2 fans can be used to bring room air into the enclosure, while the other 1 or 2 exhaust the heated air.

2. The control box is mounted in a convenient location; double-sided adhesive tape is provided.

3. The thermistors are positioned where they will sense air and/or equipment temperatures.

4. The fan and thermistor wires are connected to the control box.

5. The power supply is plugged into a convenient source of 120 volt 60Hz power.

6. The completed installation is tested.

Detailed instructions:

Note: Do not plug the power supply into an outlet until directed to do so.

Cut a 4 ½” center hole and drill 4 mounting holes for each of the fans per the enclosed drawing. The fans can be mounted either on the inside or outside surface of the enclosure; air moves towards the  label side of the fan. The fan leads may be extended, if necessary, using any appropriate 2 conductor wire. If extended, be certain that proper polarity is maintained. If there is any possibility of contact with the fan blades, install the guards supplied to prevent personal injury.

When locating the fans, remember that provision must be made to allow room air to enter the enclosure to replace the hot air being exhausted.  Locations low in the enclosure are generally preferred; the optimum arrangement is that in which air enters and passes by the heat-generating equipment on its way to the exhaust fans. Avoid locating the inlet too close to the exhaust fans as room air may enter and be immediately exhausted without cooling the enclosure and equipment. 

An air inlet improperly located or too small will prevent the System 2 or 2 + 2 from operating efficiently and quietly. 

2. Mount the control box at a convenient location. Plug the 2 or 4 fan wires into the connectors on the control box. Any fan can be plugged into any connector.
3. Thermistors control the operation of the fans. The spade-lug mounting brackets to which the thermistors are attached allow them to be easily mounted under a screw head near the hottest part of the component whose temperature is being monitored.  Alternately, the small magnets supplied can be used to “pinch” the thermistors against the equipment’s top or side covers, if they are steel. The thermistor in the hotter location will control all fans; this is useful where temperatures must be monitored in 2 locations, as when a theater amplifier is located in one section of a cabinet, and a distribution amp is located in another compartment, or the second thermistor is used to sense the temperature of a TiVo, or satellite receiver, while the first monitors an amplifier or receiver. Plug one thermistor probe into connector TH1, the other into TH2.
4. The System 2 or 2 + 2 is powered by a wall-type power supply. Do not plug it into a switched outlet; use an AC outlet which is always on to allow the fans to run after the other equipment has been turned off.  If possible, use an outlet on the same circuit that powers the equipment producing the most heat. If this circuit should fail, the ventilation will cease, but the heat source(s) will also turn off. If the System 2 or 2 + 2 is powered from a different circuit, it is possible that that circuit could lose power while the equipment in the enclosure continued to produce heat.

Operational test:

Plug the power supply into a live outlet. Plug the power supply output lead into the female connector attached to the control box.  The green LED will light to indicate that power is present.  The fans will turn at full speed for a few seconds as the control circuit initializes. They will then stop if the temperature is below approximately 80 degrees. As the temperature at the thermistor rises past approximately 80 degrees (F), the fans will begin to turn at a moderate speed, increasing as the temperature increases. A red LED will indicate that the fans are turning; its brightness will vary with fan speed. It may flash or light steadily, depending on temperature.
When the enclosure temperature falls, the fans will slow down, stopping when the temperature falls below approximately 76 degrees Fahrenheit.  Note that it is normal for the fans to begin – or stop - turning at slightly different temperatures, due to manufacturing variations in each fan.  It is also normal for them to "hunt" a bit as the temperature approaches their turn-on point.

· Please note: It is increasingly common for the fans to remain on continuously, due to the heat given off by satellite receivers, cable boxes, and PVRs, even when these devices are not is use. 
ATM System 2 & 2+2 fan mounting details 

[image: image4.wmf][image: image5.jpg]ACTIVE THERMAL
MANAGEMENT





[image: image2.wmf]
� EMBED AutoSketch.Drawing.6  ���








25570 Rye Canyon  Rd.                                        Valencia, California  91355

(661) 294-7999  voice
                                                        (661) 294-1115 fax


techinfo@activethermal.com                                     www.activethermal.com

_1105530938.pcx

